## Sheet1
UV Treatment
UV Sensor Calibration Worksheet
PWS Name:
Facility Name:
PWSID:
Facility ID:
Reporting Period:
Date | Reactor Number | Duty Sensor Number | Duty Sensor Operating Time | Reference Sensor Serial Number | Duty Sensor Reading1 | Reference Sensor Reading1 | Calibration Ratio ([A]/[B]) | Calibration Ratio ≤ 1.2? ([C] ≤ 1.2?) | Sensor Correction Factor Used | If CF is used, [C] - 0.2 ≤ CF?
|  |  | (hr) |  |  |  |  | (Y/N) |  | (Y/N)
[5 empty] | [A] | [B] | [C]
1If three duty sensor and reference sensor readings are taken, the mean of the readings can be used.
Number of UV sensors checked:
Number of UV sensors out of calibration:
Number of UV sensors sent to manufacturer to be recalibrated, as documented below:
UV Intensity Sensors Sent to Manufacturer for Calibration
Sensor Serial Number |  | Date Sent |  | Date Received
where:
SDuty is the duty UV sensor reading
SRef is the reference UV sensor reading
𝐶𝑎𝑙𝑖𝑏𝑟𝑎𝑡𝑖𝑜𝑛 𝑅𝑎𝑡𝑖𝑜= 𝑆_𝐷𝑢𝑡𝑦⁄𝑆_𝑅𝑒𝑓
𝑆𝑒𝑛𝑠𝑜𝑟 𝐶𝑜𝑟𝑟𝑒𝑐𝑡𝑖𝑜𝑛 𝐹𝑎𝑐𝑡𝑜𝑟= 𝑆_𝐷𝑢𝑡𝑦⁄𝑆_𝑅𝑒𝑓 − 0.2
where:
SDuty is the duty UV sensor reading
SRef is the reference UV sensor reading
State Logo